## Slide 1
A latent heat pump (LHP) technology
with ice slurry as media
How ice slurry technology can unlock the electrification of winter heating in Northern Europe
Laboratory of Energy Storage Technology
Guangzhou Institution of Energy Conversion, Chinese Academy of Sciences
Ziping Feng（Ph. D, Prof.）
Email: fengzp@ms.giec.ac.cn
Mobile: +86-13570091132

## Slide 2
Contents
1, Ice slurry generating process and its application
2, The principle of latent heat pump with ice slurry as media
3, Economical efficiency of latent Heat Pump

## Slide 3
Ice Slurry Generating Process: Type 1-Indirect Cold Source
-3℃
-1℃
≤0.5℃
-2℃
0℃
PHE (Subcooled Water to Glycol Solution
Crystallizing Interrupter
Ice Crystal Filter
Water intake pipe
Ice Slurry Pipe
Water Layer
Ice-Rich Layer
Chiller
Glycol Pump
Crystallizing Tank
Ultrasonic Generator
Water Pump

## Slide 4
Ice Slurry Making Process: Type 2-direct Cold Source
-3℃
-1℃
≤0.5℃
-2℃
0℃
PHE (Subcooled Water to Glycol Solution
Crystallizing Interrupter
Ice Crystal Filter
Water intake pipe
Ice Slurry Pipe
Water Layer
Ice-Rich Layer
Crystallizing Tank
Ultrasonic Generator
Water Pump
Throttle Valve
Condenser
Chiller
Glycol Pump

## Slide 5
More than 30 demonstration projects thermal storage with ice slurry have been operated in China since 2009.
The total installed capacities have been accumulated to 15,000 USRT (52,000 kW).

## Slide 6
Ice Slurry in tank

## Slide 7
Dynamic Ice Slurry Unit (DISU)
——Indirect type: DISU-R
Not include chiller
A secondary refrigerant loop (glycol solution) is necessary to link the DISU-R with a third-party chiller
The refrigerating capacities are from 50~450 Rt (175~1580 kW)
The chiller’s evaporating temp. is as high as -5.5℃
COP of the system is as high as 3.0

## Slide 8
DISU
——direct type: DISU-D
Include chiller
No secondary refrigerant loop (glycol solution)
The semi-welded plate heat exchanger for subcooled water is just the flooded evaporator of the chiller
The refrigerants can be chosen form R717 (Ammonia) and R507
The refrigerating capacities are from 20~250 Rt (70~900 kW)
DISU-D
DISS system with DISU-D
The chiller’s evaporating temp. is as high as -3℃
COP of the system is as high as 4.0

## Slide 9
1. Applications in Air Conditioning
Concept of Ice Thermal Storage A/C System
System Sketch of A/C Applying DISU-R

## Slide 10
Pasteurized milk processing using ice slurry
Chicken cooling (to 4℃) using ice slurry
4℃ Milk
0~1℃ fresh water (from ice slurry tank)
2. Applications in Industrial Cooling
Pasteurized milk with higher temp.
Water back into ice slurry tank

## Slide 11
Applications in Industrial Cooling
Milk
Meat
Sea food
Vegetable
Beverage
Ice Slurry of Fresh Water  Optimal industrial cooling source
Ice Slurry of Fresh Water – Very close to 0℃ – Easy to Cool the products to 4℃
SAFE
SANITARY
SAVING
STABLE

## Slide 12
So far, more than 5 dairy factory cases which use ice slurry (fresh water) as cooling source have been brought into operation successfully in China.

## Slide 13
Contents
1, Ice slurry generating process and its application
2, The principle of latent heat pump with ice slurry as media
3, Economical efficiency of latent Heat Pump

## Slide 14
What is a Latent Heat Pump (LHP)?
Based on the experience of thermal storage, we found that ice slurry can be used for heating in winter season. Thus, a so called “latent heat pump” is developed and has been successfully used for the heating of a residential building.
The theory of Latent Heat Pump is: in cold region, if we use traditional water/ground source heat pumps to provide heat, we can obtain less than 5 kcal/kg sensible heat from the 5℃ water source (with 5-degree temperature difference). But, if we further change water into ice slurry, then we can obtain additional 85 kcal/kg latent heat from water, which is almost 18 times to that of a traditional water/ground source heat pump. Also, the amount of circulation water is only 1/18 comparing to a common water source heat pump.
It should be mentioned that, this technology can be realized only with ice slurry because the ice should be removed away from the heat exchanger surface immediately whenever it is generated.

## Slide 15
 | Average daily water consumption kg/(m2.day) |  |  | 
 | Harbin | Beijing | Wuhan | Zhengzhou
Low-rise residential | 12.37 | 10.48 | 8.28 | 8.65
Multi-storey residence | 7.95 | 6.98 | 5.52 | 6.06
Office building | 5.15 | 4.37 | 3.45 | 3.60
Hospital | 12.37 | 11.35 | 8.83 | 10.38
Hotel | 10.60 | 9.60 | 7.72 | 8.65
Shopping mall | 6.18 | 5.67 | 4.41 | 5.19
Daily water consumption for a Latent Heat Pump (per m2)
For a 200m2 house, 1-2 ton water is enough for 1 day.

## Slide 16
Type 1: Abandoned Type Latent Heat Pump
Water intake under ice in rivers, lakes and seas
DISU
Filter
Ice separated from slurry and abandoned
Glycol loop
Heat pump
Cooling tower（Only runs in summer）
Heating users
Cooling users
If the building is nearing to the water source, then we can directly abandon the ice slurry to water source.

## Slide 17
Ice slurry storage pool
Type 2: Storage Type Latent Heat Pump
DISU
Water supplement
Heating users
Cooling tower（Only runs in summer）
Heat pump
Glycol loop
Cooling users
Solar energy or other low grade heat energy
If the building is not near to the lake or river, then we can use a water tank to keep ice slurry, and ice slurry can be melted during the daytime by solar energy. In this case, even the tap water can be used as heat source.

## Slide 18
Possible application methods-1,for home heating in EU
The tap water can be used, for example, 1-2 tons per day. This cost should not be too much for a British family.
The initial cost of the latent heat pump is a little high than the common heat pump, but not too much. However, the heating ability could be guaranteed in cold season.
If the outdoor temperature is above the frozen point, Ice slurry will be melt by sunshine during the daytime, so that the tape water can be recycled.
If the outdoor temperature is under the frozen point, the ice slurry can be used to build a small ski slope for children, or used to build snowman, it is also a good point for family.

## Slide 19
Possible application methods-2,for commercial buildings
For those buildings near to the water source (river, ocean, or there is a swimming pool), the latent heat pump is a good choice. The ice slurry can be directly poured into the rive, ocean, or the swimming poor.
If the building is far away from the water source, tap water can also be used.
A problem is where to deposit too much ice during the peak days. One possibility is to build a underground pool for seasonal cold energy storage, its efficiency should be higher than the seasonal high temperature heat storage with a ground pool due to the less temperature difference with ground.

## Slide 20
A “latent heat pump” has been successfully used for the heating of a 25000 m2 residential building in Nanjing province, it shows an excellent performance.
The latent heat pump with ice slurry can be used for anywhere the heating system is required, particularly to combine with water source or ground source heat pumps.
A demonstration project in Nanjing city

## Slide 21
Original ground source
heat pump
Ice slurry generating unit
Glycol solution
Ice slurry tank
The principle diagram of the demonstration project

## Slide 22
Latent heat pump Dynamic ice slurry unit
Ice/water separating unit pumps
Ice slurry

## Slide 23
Contents
1, Ice slurry generating process and its application
2, The principle of latent heat pump with ice slurry as media
3, Economical efficiency of latent Heat Pump

## Slide 24
Representive cities and their yearly average temperature
Harbin
Beijing
Zhengzhou
Nanjing
Wuhan
45ºN
30ºN
35ºN
25ºN
40ºN
46ºN (0~11℃)
40ºN(9~19℃)
34ºN (12~22℃)
32ºN (13~22℃)
31ºN (13~22℃)
Latitude

## Slide 25
Average COP of Latent Heat Pump in these cities
Water Temperature/℃ | Harbin | Beijing | Zhengzhou | Wuhan | Nanjing
0≤ tice＜3 | 4.2 | 4.3 | - | - | -
3≤ tice＜6 | 4.4 | 4.5 | 4.6 | 4.6 | 4.6
6≤ tice＜9 | 4.9 | 4.8 | 4.9 | 4.9 | 4.9
9≤ tice≤12 | 5.2 | 5.3 | 5.3 | 5.2 | 5.3
Assumptions：
① Refrigerant is R134a 。
② Both supercooling and superheating temperature of LHP are 5℃ and the condensing temperature is 43℃。
③ The average heat transfer temperature difference in evaporator is 3℃。
COP of LHP in different cities

## Slide 26
Harbin
Beijing
Zhengzhou
Nanjing
Wuhan
¥ 3.5 million
¥ 2.8 million
¥ 2.5 million
Air source HP
Ground source HP
Latent HP
¥ 6.0 million
¥ 3.8 million
Initial investments for varies heat pump types
45ºN
30ºN
35ºN
25ºN
40ºN
1000kW heating ability

## Slide 27
Operating costs for varies heat pump types
73
27
29
55
25
27
27
14
14
9
7
7
9
4
7
169
51
67
137
52
66
64
32
33
34
26
26
34
17
17
Electricity costs per m2
(yuan)
Harbin
Beijing
Zhengzhou
Nanjing
Wuhan
45ºN
30ºN
35ºN
25ºN
40ºN
Air source HP
Ground source HP
Latent HP
Total electricity costs during heating period
(X10000 yuan)
1000kW heating ability

## Slide 28
The initial cost recovery period of Latent Heat Pump (Comparing with Air source HP)
Harbin
Beijing
Zhengzhou
Nanjing
Wuhan
45ºN
30ºN
35ºN
25ºN
40ºN
4.2year
2.3year
10.8year
13.9year
19.9year
0.3year
1.4year
4.1year
5.1year
7.4year
Latent HP
Ground source HP
1000kW heating ability

## Slide 29: Thank you for your attention
Ziping Feng
Phone: +86-13570091132
E-Mail: fengzp@ms.giec.ac.cn